Incentive & Measure Specifications

Commercial Energy Solutions

EasySave Program

Prescriptive Incentives

| RETROFIT LIGHTING |  |
| --- | --- |
| T12 to Premium T8 Lighting | $0.15 per kWh saved |
| Delamping | $0.15 per kWh saved |
| HID to Linear Fluorescent Lighting | $0.15 per kWh saved |
| LED Lighting | $0.125 per kWh saved |
| CFL Screw-in | $0.03 per kWh saved |
| CFL Hardwired | $0.15 per kWh saved |
| Induction Lighting | $0.15 per kWh saved |
| Exit Signs | $0.15 per kWh saved |
| Daylighting Controls | $0.15 per kWh saved |
| Occupancy Sensors | $0.15 per kWh saved |

| HVAC |  |
| --- | --- |
| AC Units | $125 to $675 per unit |
| Heat Pumps | $125 to $675 per unit |
| Economizer | $120 to $200 per unit |
| Programmable Thermostats | $50 per thermostat |
| HVAC EMS System | $0.15 to $ 0.35 per square foot |
| Variable Refrigerant Flow Systems | $50 per ton |

| REFRIGERATION |  |
| --- | --- |
| Strip Curtains | $5 per square foot |
| Anti-Sweat Heater Controls (low & medium temp) | $17 per linear foot of case |
| Evaporator Fan Motors (ECM) | $100 per motor |
| Evaporator Fan Motors (ECM) with Controls | $175 per motor |
| Automatic Door Closer | $40 per closer |
| Vending Machine Controls (Reach-in and Snack Machine) | $75 per controller |
| Vending Machine Controls (Beverage) | $150 per controller |

| OTHER MEASURES |  |
| --- | --- |
| Variable Speed/Frequency Drives | $75 per horsepower |
| Shade Screens | $2 per square foot |
| Plug-Load Smart Strips | $10 per strip |

* Rebates are capped at 75% of incremental cost

Measure Specifications

All equipment removed under the program must be recycled or disposed of in compliance with local requirements. Documentation of disposal may be requested by program staff.  A manufacturer’s specification sheet and invoice may be requested for any installed measure.

Lighting

T12 to Premium T8 Lighting

This measure consists of replacing existing T12 lamps and magnetic ballasts with premium reduced wattage 25-watt or 28-watt T8 lamps and electronic ballasts or 32-watt High Performance lamps and electronic ballasts. 4-foot lamps and ballasts shall be Consortium for Energy Efficiency (CEE) listed as either Reduced Wattage or High Performance T8.

For CEE Commercial Lighting Specifications and Qualifying Product Lists please visit:

http://library.cee1.org/content/commercial-lighting-systems-initiative

http://library.cee1.org/content/commercial-lighting-qualifying-products-lists/

Ballasts for 2-foot, 3-foot, 4-foot non-CEE listed, or 8-foot lamps must have a power factor (PF) ≥ 0.90. In addition, 2-foot, 3-foot, and 4-foot non-CEE listed lamps must have a CRI ≥ 80 and must either have a ballast factor ≤ 0.78 or have a mean lumens per watt of ≥ 90. 4-foot lamps also have a minimum lamp life ≥ 24,000 hours and a lumen maintenance of 94%.  8-foot lamps must have a CRI > 80 and lamp nominal wattage of ≤ 57 watts and mean lumens per watt of ≥ 90.  Ballasts for 4-foot lamps must have total harmonic discharge (THD) ≤ 20% at full light output.  For 2- and 3-foot lamps, ballasts must have THD ≤ 32% at full light output.  Electronic ballast for 2-foot, 3-foot, 4-foot non-CEE listed, and 8-foot lamps must be high frequency (≥ 20 kHz), UL listed, and warranted against defects for 5 years.

Delamping

Delamping is the permanent removal of existing fluorescent lamps.  Unused lamps, lamp holders, and ballasts must be permanently removed from the fixture to claim the delamping rebate.  This measure is applicable when retrofitting T12 to T8, T5 or LED or simply delamping a T8 fixture.  Only removing T12s from fixture is not eligible for a rebate.

HID to Linear Fluorescent Lighting

This measure consists of replacing existing metal halide (MH) and high pressure sodium (HPS) fixtures with new fixtures with at least two high output T8 or T5 lamps along with high output electronic ballasts. Recommended combinations for existing MH/HPS fixtures are:

- 150 watts to 249 watts - replaced with either 2-lamp 4-foot or 4-lamp 2-foot linear fixtures.

- 250 watts to 399 watts should be replaced with 3-lamp linear fixtures.

- 400 watts to 749 watts should be replaced with 4-lamp T5HO or 6-lamp T8HO linear fixtures.

- 750 watts to 999 watts should be replaced with 6-lamp T5HO or two (2) 6-lamp T8HO linear fixtures.

- 1,000 watts or more should be replaced with two (2) 4-lamp T5HO linear fixtures.

All fixtures must have a reflector with a minimum of 90% reflectivity.  The new lamps must have a color rendering index (CRI) of ≥ 80.  The electronic ballasts must be high frequency (≥20 kHz), UL listed and warranted against defects for 5 years.  Ballasts must have a power factor (PF) of ≥0.90.  Ballasts for 4-foot lamps must have a total harmonic discharge (THD) of ≤20% at full light output.  Low Pressure Sodium (LPS) lamps are not eligible to be replaced under this prescriptive incentive.

LED Lighting

LED screw-in lamps must replace incandescent or halogen lamps on a one-for-one basis.  Reflector lamps must be R, BR or PAR series. It is expected that a wattage reduction of 60% be achieved to obtain a rebate.  Linear LED lamps may replace existing T12 or T8 lamps. It is expected that a wattage reduction of 40% be achieved to obtain a rebate. Metal halide and high pressure sodium fixtures may be retrofitted with appropriate LED lamps or replaced with an appropriate LED fixture. It is expected that a wattage reduction of 60% be achieved to receive a rebate.  All LED lamps, linear tubes or fixtures must be either listed as a qualified product with DesignLights Consortium or Energy Star certified.

Compact Fluorescent Lamps (CFLs)

This incentive applies to screw-in or hardwired compact fluorescent lamps and applies only if an incandescent lamp is being replaced.  All screw-in CFLs must be ENERGY STAR®-certified.  Any lamp receiving a retail buy-down by TEP is not eligible.  The lamp/ballast combination must have an efficacy ≥ 40 lumens per watt (LPW).  For screw-in CFLs, electronic ballasts are required for lamps ≥ 18 watt.  For hardwired CFLs, only complete new fixtures or modular retrofits with hardwired electronic ballasts qualify.  The CFL ballast must be programmed start or programmed rapid start with a PF ≥ 90 and THD ≤ 20%.

Induction Lighting

This measure consists of replacing existing metal halide (MH), mercury vapor (MV) or high pressure sodium (HPS) fixtures with new induction lighting fixtures. In addition, lamps must have a CRI ≥ 80, an expected life of 70,000 hours or greater, and must save at least 40% from the MH/HPS lamp wattage.

Exit Signs

High-efficiency exit signs must replace or retrofit an existing incandescent or CFL exit sign. Electroluminescent and light-emitting diode (LED) exit signs are eligible under this category.  Non-electrified and remote exit signs are not eligible.  All new exit signs or retrofit exit signs must be UL or ETL listed, have a minimum lifetime of ten years, and have an input wattage ≤ 5 watts.  A minimum warranty of five years is required.

Daylighting Controls

Eligible controls shall consist of a photosensor that controls on/off, stepped or continuous dimming ballasts.  The on/off controller should turn off artificial lighting when the interior illuminance meets the desired indoor lighting level. The stepped controller generally dims the artificial lighting 50% when the interior illuminance levels reach 50% (example for a 2-step controller) of the desired lighting levels. Continuous or dimming controllers dim artificial lighting proportional to the available ambient light. All types of daylight sensor controls are required to be commissioned in order to ensure proper sensor calibration and energy savings.  Systems that allow on/off overrides are not eligible.

Occupancy Sensors

Only passive infrared and/or ultrasonic detectors are eligible.  Wall box and wall-, ceiling- or fixture-mounted sensors must be hardwired to control interior lighting fixtures.

HVAC

Air-Cooled Air Conditioning and Heat Pumps

New air-cooled air conditioning units or heat pumps between 2 and 5 tons with a Seasonal Energy Efficiency Ratio (SEER) rating of at least 15 are eligible for an incentive. They can be either split systems or single packaged units. All packaged and split system cooling equipment must meet Air-Conditioning, Heating and Refrigeration Institute (AHRI) standards (210/240, or 340/360), be UL listed, and use a minimum ozone-depleting refrigerant (e.g., HCFC or HFC). Evaporative coolers and water source heat pumps are not eligible.

Economizers

The economizer must be capable of modulating to 95% open.  Retrofits and replacement of existing HVAC units are eligible. Replacements of existing economizers are not eligible for rebates unless the existing economizer has been non-functional for more than two (2) years.  Rebates are not available for economizers that are required per ASHRAE 90.1-2010.

Programmable Thermostats

Equipment must replace a non-programmable thermostat.  Programmable thermostats must be capable of 7-day, 5-2 or 5-1-1 programming. Programmable thermostats installed in hotel and motel guest rooms are not eligible for this rebate. Thermostats for evaporative coolers are not eligible.

HVAC EMS System

This measure is for installing an energy management system to replace thermostats, pneumatic controls or an existing direct digital control (DDC) system.  This measure is paid by the square foot of the area controlled.  (Please contact us at 1-866-324-5506 or ces@tep.com for more details.)

Variable Refrigerant Flow (VRF) HVAC Systems

New VRF Air Conditioning or Heat Pump systems installed as replacements for existing  HVAC units/systems that meet or exceed the qualifying Energy Efficiency Ratio (EER) and Integrated Energy Efficiency Ratio (IEER) are eligible for an incentive. All VRF equipment must have efficiencies that have been determined using the rating method outlined in the Air-Conditioning, Heating and Refrigeration Institute (AHRI) standard  1230-2010, be UL listed, and use a minimum ozone-depleting refrigerant (e.g., HCFC or HFC).

REFRIGERATION

Strip Curtains

New strip curtains or clear plastic swinging doors must be installed on doorways of walk-in boxes and refrigerated warehouses.  This incentive is not available for display cases or replacing existing strip curtains. Incentive is based on square foot of the opening.

Anti-Sweat Heater Controls

For this measure, a device is installed that senses the relative humidity in the air outside of the display case and reduces or turns off the glass door (if applicable) and frame anti-sweat heaters at low-humidity conditions.  Technologies that can turn off anti-sweat heaters based on sensing condensation (on the inner glass pane) also qualify.

Evaporator Fan Motors

This measure is applicable to the replacement of an existing standard-efficiency shaded-pole evaporator fan motor in refrigerated display cases or fan coil in walk-ins with an electronically commutated motor (ECM).

Evaporator Fan Motor with Evaporator Fan Control

This measure consists of the replacement of an existing standard efficiency shaded pole evaporator fan motor without controls with an electronically commutated (EC) evaporator fan motor with controls in medium and low temperature walk-in coolers and freezers.  It must control a minimum fan load of 1/47 where the fan(s) operate continuously at full speed.  It must also reduce fan motor power by at least 75% during the compressor off-cycle.  This measure is not applicable if any of the following existing (base case) conditions apply: the compressor runs all the time with high duty cycle, the evaporator fan does not run at full speed all the time, the evaporator fan motor runs on poly-phase power, or the evaporator does not use off-cycle or time-off defrost.

Automatic Door Closers 
Automatic door closers must automatically close the main insulated door of an existing walk-in cooler or freezer. The auto-closer must firmly close the door when it is within one inch of full closure.  Only new installations are eligible for a rebate.

Vending Machine Controls – Beverage, Reach-in and Snack

The controller must include a passive infrared occupancy sensor to turn off lamps and other vending machine systems when the surrounding area is unoccupied for 15 minutes or longer.  The beverage case controls should be installed on refrigerated vending machines which contains only non-perishable bottled and canned beverages.  The reach-in cooler controller is for glass-front coolers (typically with sliding or pull-open doors) that contain non-perishable goods.  The snack machine controls are for non-refrigerated vending machines.  For refrigerated equipment, the control logic should power up the machine at two-hour intervals to maintain product temperature.

OTHER MEASURES

Variable Speed Drives on HVAC Fan and Pump

Variable speed drives (VSDs) installed on HVAC fans or pumps are eligible for an incentive. The rated connected motor horsepower must be <50 hp.  The installation of a VSD must accompany the permanent removal or disabling of any flow control devices such as inlet vanes, bypass dampers, and throttling valves to be eligible. This measure applies only to VSDs installed with an automatic control technology.

This measure does not apply to redundant or backup/standby motors that are expected to operate less than 1,200 hours per year.  Nor does it apply to variable pitch fans and forward curve with inlet guide vanes unless applicant supplies proof of kWh savings from logged or measured data

This measure does not apply to replacement of a multi-speed motor or VSDs included on a new variable speed chiller.

Shade Screens

This measure consists of installing fixed exterior mounted shading screens to windows. This rebate is available only for the retrofit of existing windows with east, south or west exposures. The shade screens must have a shading coefficient of 0.30 or less at thirty-degree profile angle.  The shading coefficient equals the Solar Heat Gain Coefficient (SHGC) x 1.15.  Interior window shades such as blinds, drapes and movable door screens are not eligible.

Plug-Load Smart Strips

New plug-load smart strips can be installed to control electricity-using equipment in offices or cubicles, including lighting, monitors, shared copiers, and/or printers. Three types of smart strips are eligible for rebates – occupancy sensors, load controlled and time controlled.  Power strips with an occupancy sensor must have passive infrared and/or ultrasonic detectors for plug-load office equipment.  Load-sensing smart plug strips detect a drop in current when a control device enters low-power mode.  Timer smart strips turn equipment on and off based on programmable timer.  This device should be used on equipment that requires a long warm-up.