## Cover
Commercial Energy Solutions
EasySave Plus
2020 Rebate Application
Prescriptive Measures for Existing Facilities
Energy Management Systems (EMS)
Submit application to:
TEP Commercial Energy Solutions
88 E Broadway Blvd
Mail Stop HQW505
PO Box 711, Tucson, AZ 85702
Tel: 1-866-324-5506
ces@tep.com
|  |  | Program updates will be posted at: | www.tepcommercialenergysolutions.com
Application Process
1. Submit a Pre-Notification Application.
2. Install the qualified technology.
3. Submit a complete, signed Final Application with all documentation.
4. Receive incentive check within 6 weeks of Final Application approval.
Last Modified: 04/28/2020
Funded by TEP customers and approved by the Arizona Corporation Commission

## EMS
TEP EasySave Plus - Prescriptive Application
Energy Management Systems (EMS) Worksheet |  |  |  |  | 2020-04-28
Project Name: | [5 empty] | TEP Account #:
Energy Management Systems Incentives
|  | Existing System Being Replaced |  |  | Tier 1 ($/SF) | Tier 2 ($/SF) | [11 empty] | 1 = Yes, 0 = No
|  | Thermostat Controlled: |  |  | 0.8 | 0.9 | [7 empty] | Tier 1 | Tier 2 |  |  | Qualify for |  |  | Area 1
|  | 1. Pneumatic Thermostats | [6 empty] | System being replaced | Direct-Expansion (DX) | Chilled Water | System Type | SF Area | Incentive $/SF | Incentive $/SF | Tier 1 Reqd Strategies | Tier 2 Reqd Strategies | Tier 1 | Tier 2 | Tier Level | Tier Rate | Incentive
|  | 2. Non-Programmable Thermostats | [5 empty] | 1 | Pneumatic thermostats | 0 | 0 | 0 | 0 | 0.8 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 3. Programmable Thermostats (Non-Networked) | [5 empty] | 2 | Non-programmable thermostats | 0 | 0 | 0 | 0 | 0.8 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Existing Controls: |  |  | 0.6 | 0.7 |  | 3 |  | 0 | 0 | 0 | 0 | 0.8 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 1. Networked Thermostats (Building-Wide Programmable) | [5 empty] | 4 | Networked thermostats | 0 | 0 | 0 | 0 | 0.6 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 2. Existing Digital Energy Management System | [5 empty] | 5 | Existing Digital EMS system | 0 | 0 | 0 | 0 | 0.6 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Yellow Box: Click in box and select from drop down menu |  |  | White Box: No entry required |  | Green Box: requires a number to be entered |  |  |  | If chilled water is selected, use higher Tier 2 for DX |  |  | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
Energy Management Systems | [8 empty] | Cooling System Type | Tier 1 | Tier 2
Control System Being Replaced |  | HVAC System | Conditioned Space SF | Incentive ($/SF) | Qualified Tier Level |  | Subtotal |  | Direct-Expansion (DX) | 5 | 7
Pneumatic Thermostats | [8 empty] | Chilled Water | 5 | 10
Non Programmable Thermostats
Programmable Thermostats
Networked Thermostats | [8 empty] | Yes
Existing Digital EMS System
[6 empty] | Energy Management Systems Total | 0
Implemented and Tier Requirements
Enhanced Strategies Required To Reach Tier 1*- |  |  |  | *Four Enhanced Control Strategies plus Unoccupied Temperature Setback, which is mandatory, are required from the list below.
Enhanced Strategies Required To Reach Tier 2 -
Enhanced Strategies Implemented -
Enhanced Control Strategies
Index | Avanced Control Strategy |  | Implemented | System | Explanations and Notes
1 | Chilled Water Temperature Reset |  |  | Chilled Water
2 | Chiller Compressor Sequencing |  |  | Chilled Water
3 | Condenser Water Temperature Reset |  |  | Chilled Water
4 | Cooling Tower Fan Speed Control |  |  | Chilled Water
5 | Cooling Tower Fan Staging |  |  | Chilled Water
6 | Distribution Pump Speed Control |  |  | Chilled Water
7 | Distribution Pump Sequencing |  |  | Chilled Water
8 | Secondary Chilled Water Loop Pressure |  |  | Chilled Water
9 | Deadband Control for Heating and Cooling |  |  | Either | Minimum 5°F
10 | Demand Control Ventilation |  |  | Either
11 | Static Pressure Reset |  |  | Either
12 | Summer/Winter Volume Change |  |  | Either
13 | Supply Air Temperature Reset |  |  | Either
14 | Unoccupied Temperature Setback |  |  | Either | Mandatory for Tier 1
15 | Zone-by-Zone Scheduling |  |  | Either
16 | Cooling Lockout on OAT |  |  | Either | Outside Air Temperature (OAT)
17 | Heating Lockout on OAT |  |  | Either
18 | Improved Outside Air Volumne Control |  |  | Either | Direct outdoor air measurement, volumetric fan tracking, fixed damper position, or plenum pressure differential.
19 | Night Ventilation Purge |  |  | Either
20 | Optimum Economizer Control |  |  | Either
21 | Limit Outside Air |  |  | Either | During Morning Warm-Up/Cool Down Cycle
22 | Optimal Start/Stop |  |  | Either
23 | Hot Water Reset |  |  | Either
All work shall be performed in accordance with all applicable professional standards and comply with all applicable federal, state, and local laws, ordinances,codes and regulations.
Project Completion Date
[6 empty] | Energy Management Systems Total | 0
Incentives cannot exceed 50% of incremental measure cost.
Project Name: |  | Energy Management Systems (EMS)
Enter Project Name on Page 1
TEP Account #: | Enter Act # on Page 1
Measure Specifications
Buildings and spaces within buildings that are not mechanically cooled are not eligible for the EMS rebate. EMS controls for electric resistance heating only systems may be submitted using the Custom Application. Buildings and spaces that are continuously occupied are only eligible for the Tier 2 incentive. Projects which are primarily “integration” projects that overlay existing EMS control systems are not eligible for this measure.
Measure: Install Energy Management System (EMS) to optimize system operation.
• Replace existing electric (non-programmable) or pneumatic thermostats — Tier 1 incentive of $0.80 per square foot of controlled and conditioned space. Meeting Tier 2 specification requirements qualifies for $0.90 per square foot of controlled and conditioned space.
• Replace existing programmable thermostats or digital EMS – Tier 1 incentive of $0.60 per square foot of controlled and conditioned space. Meeting Tier 2 specification requirements qualifies for $0.70 per square foot of controlled and conditioned space.
• Central-plant optimization projects must be applied for under Custom program.
Minimum EMS Requirements:
• Central Time Control
• Graphic operator interface
• Trending capability
• Web-based interface with PC-based controls
• Holiday schedules must be entered for a minimum of one year. For premises with varying schedules (i.e. schools, seasonal occupancy) the occupancy schedules must be entered for a minimum of one year.
• For facilities over 100,000 square feet, a pre-inspection is required to document existing conditions.
Tier 1 EMS requirements:
• Minimum setback temperature of at least 8°F in both heating and cooling
• Minimum setback period must exceed 2,200 hours per year
• Implement at least four enhanced control strategies not including unoccupied temperature setback (which is mandatory for Tier 1).
• Hotel/Motels and other continuously occupied spaces are not eligible for Tier 1 EMS incentives. Hotels and Motels using occupancy based control can apply for the Hotel Room Occupancy Controls incentive on the HVAC worksheet.
Tier 2 EMS requirements:
• For direct-expansion (DX) systems: implement at least seven enhanced control strategies.
• For chilled water (CW) systems: implement at least ten enhanced control strategies.
• For facilities with both DX and CW systems all areas must implement at least ten enhanced control strategies to meet Tier 2 incentive level.
Required documentation:
• Documentation shall be submitted in electronic format along with application form.
• Documentation supporting the conditioned space on the application. This information can typically be found on facility drawings or a spreadsheet indicating the space measurements.
• System points list that shows all components integrated to EMS.
• EMS manufacturer specs
• Sequence of operation clearly indicating:
o Occupied, setback time periods and established temperatures.
o Occupied, unoccupied, and holiday scheduling
o On / off control of motors (as applicable)
o Enhanced strategies implemented
o EMS screenshots displaying system settings (temperature set points, schedules, etc.)
Pre and post inspections may be required to verify stated conditions.
The following additional documentation may be requested:
• Documentation of the age of the existing EMS.
• Photo verification of the existing thermostats or EMS controls.
• Confirmation of the programming functionality.
. | . | . | . | . | . | .
Note on C18: Select from the drop down list.