## Room Count
Project Name |  |  |  |  | SHEET TIPS: | ▪ This sheet allows reviewers to verify quantities on worksheets and for a proper inspection to be performed without assistance
Put any comments here | [5 empty] | ▪ Enter a new line for each room or area. Rooms with multiple fixture/bulb models will require multiple lines
[6 empty] | ▪ BULB SWAP ---> All wattages are individual bulb wattage | [7 empty] | FIXTURE SWAP---> All Wattages are fixture input wattage |  |  |  | Reference Count |  |  |  | DNVGL USE
[6 empty] | ▪ DELAMP ---> Permanent reduction of qty of lamps/fixtures | [7 empty] | OCC SENSOR ---> Enter Qty of Occ Sensor per line
Click for fixture input wattages |  |  | Answer this before wattage! |  |  | ▪UNISOURCE Electric projects are always on a custom worksheet | [7 empty] | ▪TIPS - Hover over "Tip" to see help for a column
Room or Area Name | Interior or Exterior? | Prescriptive or Custom Worksheet? | Worksheet Row # | Bulb or Whole Fixture Being Replaced? | Fixture/Bulb Type | Wattage - Bulb | Wattage - Fixture | Qty Fixtures | Bulbs per Fixture | New Fixture / Bulb Model # | Wattage - Bulb | Wattage - Fixture | Qty Fixtures | Bulbs per Fixture | Qty De-Lamping (enter # Bulbs) | Qty of Ocupancy Sensors to be installed? |  | PRE Bulb Count | POST Bulb Count | PRE Fixture Count | POST Fixture Count | Occ Sensor Watts/ Line | Invoice
Tip |  | Tip | Tip | Tip | Tip | Tip | Tip | Tip | Tip | Tip | Tip | Tip | Tip | Tip | Tip | Tip
Fixture Location |  |  |  | Existing Lighting | [5 empty] | New Lighting |  |  |  |  | Delamp | Occ | COMMENTS
Ex: Conference Room | Int | Pres | 30 | Bulb | 2L T8 4' | 32 |  | 4 | 2 | T4815/850/AB/LED/10 | 15 |  | 4 | 2 |  | 1 |  | 8 | 8 | 4 | 4 | 120
Ex:: Sales Floor | Int | Cust | 38 | Fixt | 4L T8 4' |  | 113 | 30 | 4 | RT24FP (2x4 Panel) |  | 30 | 30 | 1 | 40 |  |  | 120 | 30 | 30 | 30 | 0
Ex: Parking Lot | Ext | Pres | 46 | Fixt | MH Shoebox 250W |  | 295 | 20 | 1 | PLLD-30K100 |  | 100 | 20 | 1 |  |  |  | 20 | 20 | 20 | 20 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[18 empty] | 0 | 0 | 0 | 0 | 0
[15 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
Note on Y6: Bird, Craig: Qty is per line, does not consider # of Occ sensors per line item
Note on A7: Bird, Craig: Room or Area Name. One line per area per fixture/bulb type. Areas with multiple fixture/bulb models will require multiple lines. For example If 'Office 1' has 2L T8's and Recessed Cans it will have 2 lines. Different wattages will also have seperate lines.
Note on C7: Bird, Craig: Will this line item be on the Prescriptive or Custom worksheet? UniSource Electric measures are always custom
Note on D7: Bird, Craig: Once the worksheet is filled out, the row # should be entered here.
Note on E7: Bird, Craig: FILL THIS FIELD OUT BEFORE WATTAGE. Are you just changing bulbs or will you be replacing the entire fixture?
Note on F7: Bird, Craig: Please describe the type of existing fixture. More examples CFL 26W, PAR30 15W, HPS 600W, High Bay MH 250W etc
Note on G7: Bird, Craig: Single bulb wattage only. Printed on bulb.
Note on H7: Bird, Craig: Fixture wattage is the input wattage including ballast. See "Input Wattage" tab for default input fixture wattage.
Note on I7: Bird, Craig: NOT BULB QTY. Always enter qty of fixtures. Bulb counts are shown to right of table after filling out 'Bulbs per Fixture'
Note on J7: Bird, Craig: If fixture has one bulb, enter 1
Note on K7: Bird, Craig: Enter the model number from the specification sheet
Note on L7: Bird, Craig: Single bulb wattage only. Printed on bulb.
Note on M7: Bird, Craig: Fixture wattage is the input wattage including ballast. See "Input Wattage" tab for default input fixture wattage.
Note on N7: Bird, Craig: NOT BULB QTY. Always enter qty of fixtures. Bulb counts are shown to right of table after filling out 'Bulbs per Fixture'
Note on O7: Bird, Craig: If fixture has 1 bulb or is integrated LEDS(ie panels or LED Strips), enter 1
Note on P7: Bird, Craig: Enter the number of bulbs that will be permanantely reduced and not replaced. Example (10) 4L T8's reduced to (10) 2L T8's = 20 bulbs delamped OR 20 MH Fixtures to 10 LED Fixtures = 10 bulbs delamped
Note on Q7: Bird, Craig: Enter number of Occ Sensors for the line item. Pays per installed watt. If more then 1 sensor is installed we will divide total watts by # of sensors

## Input Wattage
Select Product | T8 |  |  | FIXTURE INPUT WATTAGES
BALLAST TYPE
|  | Magnetic |  | Electronic | T8 Standard Ballast |  |  | T8 High Efficiency Ballast
Product | # Lamps | Standard Mag | Energy Saving Mag | Electronic | Low BF | Normal BF | High BF | Low BF | *default Normal BF | High BF | Product | Description | # Lamps | Std Mag | Energy Saving Mag | Electronic | STD LBF | STD NBF | STD HBF | HE LBF | HE NBF | HE HBF | Product List | Tip | Helper 1 | Helper 2 | Helper 3
F13T8 1' 13W | 1 | – | 17 | – | – | – | – | – | – | – | T12 | F15T12 1.5' 15W | 1 | – | 21 | – | – | – | – | – | – | – | T8 |  | 1 |  | 108
F13T8 1' 13W | 2 | – | 36 | – | – | – | – | – | – | – | T12 | F15T12 1.5' 15W | 2 | – | 41 | – | – | – | – | – | – | – | T12 |  | 2 |  | 109
F15T8 1.5' 15W | 1 | – | 20 | – | – | – | – | – | – | – | T12 | F15T12 1.5' 15W | 3 | – | 63 | – | – | – | – | – | – | – | T5 |  | 3 |  | 110
F15T8 1.5' 15W | 2 | – | 41 | – | – | – | – | – | – | – | T12 | F20T12 2' 20W | 1 | – | 21 | – | – | – | – | – | – | – | CFL |  | 4 |  | 111
F17T8 2' 17W | 1 | – | 24 | – | – | 18 | – | 13 | 15 | 20 | T12 | F20T12 2' 20W | 2 | – | 53 | – | – | – | – | – | – | – | HPS |  | 5 |  | 112
F17T8 2' 17W | 2 | – | 45 | – | – | 31 | – | 27 | 30 | 39 | T12 | F20T12 2' 20W | 3 | – | 64 | – | – | – | – | – | – | – | MV |  | 6 |  | 113
F17T8 2' 17W | 3 | – | 64 | – | – | 45 | – | 40 | 45 | 59 | T12 | F20T12 2' 20W | 4 | – | 91 | – | – | – | – | – | – | – | MH |  | 7 |  | 114
F17T8 2' 17W | 4 | – | 83 | – | – | 57 | – | 53 | 60 | 78 | T12 | F24T12 2' 35W HO | 1 | – | 64 | – | – | – | – | – | – | – | MV Canopy/Soffit |  | 8 |  | 115
F25T8 3' 25W | 1 | – | 30 | – | – | 24 | – | 20 | 22 | 29 | T12 | F24T12 2' 35W HO | 2 | – | 95 | – | – | – | – | – | – | – | MH Canopy/Soffit |  | 9 |  | 116
F25T8 3' 25W | 2 | – | 62 | – | – | 43 | – | 39 | 44 | 58 | T12 | F24T12 2' 35W HO | 3 | – | 148 | – | – | – | – | – | – | – | HPS Canopy/Soffit |  | 10 |  | 117
F25T8 3' 25W | 3 | – | 87 | – | – | 63 | – | 63 | 72 | 86 | T12 | F24T12 2' 35W HO | 4 | – | 183 | – | – | – | – | – | – | – | MV Wall Pack |  | 11 |  | 118
F25T8 3' 25W | 4 | – | 116 | – | – | 85 | – | 85 | 74 | 111 | T12 | F30T12 2.5' 42W HO | 1 | – | 67 | – | – | – | – | – | – | – | MH Wall Pack |  | 12 |  | 119
F25T8 4' 25W | 1 | – | – | – | – | 26 | – | 20 | 22 | 29 | T12 | F30T12 2.5' 42W HO | 2 | – | 95 | – | – | – | – | – | – | – | HPS Wall Pack |  | 13 |  | 120
F25T8 4' 25W | 2 | – | – | – | – | 43 | – | 39 | 44 | 58 | T12 | F21T12 3' 21W | 1 | – | – | 25 | – | – | – | – | – | – | CFL Pin |  | 14 |  | 121
F25T8 4' 25W | 3 | – | – | – | – | 63 | – | 59 | 66 | 94 | T12 | F21T12 3' 21W | 2 | – | – | 49 | – | – | – | – | – | – |  |  | 15 |  | 122
F25T8 4' 25W | 4 | – | – | – | – | 85 | – | 78 | 88 | 115 | T12 | F24T12 3' 24W | 1 | – | 45 | – | – | – | – | – | – | – |  |  | 16 |  | 123
F28T8 4' 28W | 1 | – | – | – | – | 25 | – | 22 | 25 | 32 | T12 | F24T12 3' 24W | 2 | – | 65 | – | – | – | – | – | – | – |  |  | 17 |  | 124
F28T8 4' 28W | 2 | – | – | – | – | 48 | – | 44 | 49 | 64 | T12 | F25T12 3' 25W | 1 | – | – | 35 | – | – | – | – | – | – |  |  | 18 |  | 125
F28T8 4' 28W | 3 | – | – | – | – | 72 | – | 66 | 74 | 97 | T12 | F25T12 3' 25W | 2 | – | – | 71 | – | – | – | – | – | – |  |  | 19 |  | 126
F28T8 4' 28W | 4 | – | – | – | – | 97 | – | 87 | 99 | 129 | T12 | F25T12 3' 25W | 3 | – | – | 70 | – | – | – | – | – | – |  |  | 20 |  | 127
F30T8 4' 30W ES | 1 | – | 40 | – | – | 31 | – | – | – | – | T12 | F25T12 3' 25W | 4 | – | – | 88 | – | – | – | – | – | – |  |  | 21 |  | 128
F30T8 4' 30W ES | 2 | – | 82 | – | – | 54 | – | – | – | – | T12 | F30T12 3' 25W | 1 | – | 40 | 28 | – | – | – | – | – | – |  |  | 22 |  | 129
F30T8 4' 30W ES | 3 | – | – | – | – | 77 | – | – | – | – | T12 | F30T12 3' 25W | 2 | – | 64 | 50 | – | – | – | – | – | – |  |  | 23 |  | 130
F30T8 4' 30W ES | 4 | – | – | – | – | 104 | – | – | – | – | T12 | F30T12 3' 25W | 3 | – | 103 | 80 | – | – | – | – | – | – |  |  | 24 |  | 131
F32T8 4' 32W | 1 | – | 35 | – | – | 32 | – | 25 | 28 | 37 | T12 | F30T12 3' 25W | 4 | – | 125 | – | – | – | – | – | – | – |  |  | 25 |  | 132
F32T8 4' 32W | 2 | – | 68 | – | 52 | 59 | 77 | 50 | 56 | 74 | T12 | F30T12 3' 30W | 1 | – | 40 | 30 | – | – | – | – | – | – |  |  | 26 |  | 133
F32T8 4' 32W | 3 | – | 100 | – | 78 | 88 | 115 | 75 | 84 | 110 | T12 | F30T12 3' 30W | 2 | – | 75 | 60 | – | – | – | – | – | – |  |  | 27 |  | 134
F32T8 4' 32W | 4 | – | 131 | – | 104 | 117 | 153 | 100 | 113 | 147 | T12 | F30T12 3' 30W | 3 | – | 113 | 90 | – | – | – | – | – | – |  |  | 28 |  | 135
F32T8 4' 32W | 6 | – | – | – | – | – | – | 150 | 169 | 221 | T12 | F30T12 3' 30W | 4 | – | 138 | – | – | – | – | – | – | – |  |  | 29 |  | 136
F32T8 4' 32W | 8 | – | – | – | – | – | – | 200 | 225 | 294 | T12 | F36T12 3' 30W SLIM | 1 | – | 57 | – | – | – | – | – | – | – |  |  | 30 |  | 137
F32T8 4' 32W | 12 | – | – | – | – | – | – | 300 | 338 | 442 | T12 | F36T12 3' 30W SLIM | 2 | – | 83 | – | – | – | – | – | – | – |  |  | 31 |  | 138
F32T8 4' 32W | 14 | – | – | – | – | – | – | 349 | 394 | 515 | T12 | F36T12 3' 50W HO | 1 | – | 72 | – | – | – | – | – | – | – |  |  | 32 |  | 139
F32T8 4' 32W | 16 | – | – | – | – | – | – | 399 | 451 | 589 | T12 | F36T12 3' 50W HO | 2 | – | 110 | – | – | – | – | – | – | – |  |  | 33 |  | 140
F32T8 4' 32W | 18 | – | – | – | – | – | – | 449 | 507 | 662 | T12 | F36T12 3' 50W HO | 3 | – | 166 | – | – | – | – | – | – | – |  |  | 34 |  | 141
F32T8 4' 32W | 20 | – | – | – | – | – | – | 499 | 563 | 736 | T12 | F36T12 3' 50W HO | 4 | – | 212 | – | – | – | – | – | – | – |  |  | 35 |  | 142
F32T8 4' 32W VHLO | 3 | – | – | – | – | – | – | – | 279 | – | T12 | F42T12 3.5' 35W SLIM | 1 | – | 57 | 48 | – | – | – | – | – | – |  |  | 36 |  | 143
F32T8 4' 32W VHLO | 5 | – | – | – | – | – | – | – | 465 | – | T12 | F42T12 3.5' 35W SLIM | 2 | – | 87 | 73 | – | – | – | – | – | – |  |  | 37 |  | 144
F32T8 4' 32W VHLO | 6 | – | – | – | – | – | – | – | 555 | – | T12 | F42T12 3.5' 50W HO | 1 | – | 72 | – | – | – | – | – | – | – |  |  | 38 |  | 145
F32T8 4' 32W VHLO | 8 | – | – | – | – | 0 | – | – | 793 | – | T12 | F42T12 3.5' 50W HO | 2 | – | 126 | – | – | – | – | – | – | – |  |  | 39 |  | 146
F36T8 4' 36W | 2 | – | – | – | – | 74 | – | – | – | – | T12 | F48T12 4' 30W | 1 | – | 49 | 39 | – | – | – | – | – | – |  |  | 40 |  | 147
F48T8 HO 4' 44W | 1 | – | – | – | – | 59 | – | – | – | – | T12 | F48T12 4' 30W | 2 | – | 80 | 64 | – | – | – | – | – | – |  |  | 41 |  | 148
F48T8 HO 4' 44W | 2 | – | 120 | – | – | 98 | – | – | – | – | T12 | F40T12 4' 34W | 1 | 45 | 42 | 31 | – | – | – | – | – | – |  |  | 42 |  | 149
F40T8 5' 40W | 1 | – | 50 | – | – | 39 | – | – | – | – | T12 | F40T12 4' 34W | 2 | 84 | 67 | 60 | – | – | – | – | – | – |  |  | 43 |  | 150
F40T8 5' 40W | 2 | – | 86 | – | – | 75 | – | – | – | – | T12 | F40T12 4' 34W | 3 | 127 | 104 | 91 | – | – | – | – | – | – |  |  | 44 |  | 151
F40T8 5' 40W | 3 | – | 131 | – | – | 107 | – | – | – | – | T12 | F40T12 4' 34W | 4 | 156 | 144 | 119 | – | – | – | – | – | – |  |  | 45 |  | 152
F40T8 5' 40W | 4 | – | 171 | – | – | 116 | – | – | – | – | T12 | F40T12 4' 40W | 1 | 51 | 41 | 38 | – | – | – | – | – | – |  |  | 46 |  | 153
F60T8 HO 5' 55W | 1 | – | – | – | – | 70 | – | – | – | – | T12 | F40T12 4' 40W | 2 | 97 | 87 | 71 | – | – | – | – | – | – |  |  | 47 |  | 154
F60T8 HO 5' 55W | 2 | – | 126 | – | – | 118 | – | – | – | – | T12 | F40T12 4' 40W | 3 | 135 | 141 | 107 | – | – | – | – | – | – |  |  | 48 |  | 155
F72T8 6' 46W | 1 | – | 52 | – | – | 50 | – | – | – | – | T12 | F40T12 4' 40W | 4 | 175 | 172 | 134 | – | – | – | – | – | – |  |  | 49 |  | 156
F72T8 6' 46W | 2 | – | 97 | – | – | 88 | – | – | – | – | T12 | F48T12 4' 40W | 1 | – | 62 | 53 | – | – | – | – | – | – |  |  | 50 |  | 157
F96T8 8' 59W ES | 1 | – | – | – | – | 64 | – | 47 | 52 | 68 | T12 | F48T12 4' 40W | 2 | – | 98 | 82 | – | – | – | – | – | – |  |  | 51 |  | 158
F96T8 8' 59W ES | 2 | – | – | – | – | 104 | – | 94 | 104 | 136 | T12 | F48T12 4' 60W HO | 1 | – | 82 | 62 | – | – | – | – | – | – |  |  | 52 |  | 159
F72T8 6' 66W HO | 1 | – | – | – | – | 81 | – | – | – | – | T12 | F48T12 4' 60W HO | 2 | – | 133 | 125 | – | – | – | – | – | – |  |  | 53 |  | 160
F72T8 6' 66W HO | 2 | – | 150 | – | – | 135 | – | – | – | – | T12 | F48T12 4' 60W HO | 3 | – | 204 | – | – | – | – | – | – | – |  |  | 54 |  | 161
F96T8 8' 86W HO | 1 | – | – | – | – | 100 | – | – | – | – | T12 | F48T12 4' 60W HO | 4 | – | 263 | – | – | – | – | – | – | – |  |  | 55 |  | 162
F96T8 8' 86W HO | 2 | – | – | – | – | 160 | – | – | – | – | T12 | F48T12 4' 116W HO | 1 | – | 130 | – | – | – | – | – | – | – |  |  | 56 |  | 163
F96T8 8' 96W | 1 | – | – | – | – | – | – | 47 | 52 | 68 | T12 | F48T12 4' 116W HO | 2 | – | 230 | – | – | – | – | – | – | – |  |  | 57 |  | 164
F96T8 8' 96W | 2 | – | – | – | – | – | – | 94 | 104 | 136 | T12 | F48T12 4' 116W HO | 3 | – | 329 | – | – | – | – | – | – | – |  |  | 58 |  | 165
[11 empty] | T12 | F60T12 5' 138W HO | 1 | – | 140 | – | – | – | – | – | – | – |  |  | 59
[11 empty] | T12 | F60T12 5' 138W HO | 2 | – | 241 | – | – | – | – | – | – | – |  |  | 60
[11 empty] | T12 | F60T12 5' 50W | 1 | – | 72 | 64 | – | – | – | – | – | – |  |  | 61
[11 empty] | T12 | F60T12 5' 50W | 2 | – | 111 | 103 | – | – | – | – | – | – |  |  | 62
[11 empty] | T12 | F60T12 5' 75W HO | 1 | – | 98 | – | – | – | – | – | – | – |  |  | 63
[11 empty] | T12 | F60T12 5' 75W HO | 2 | – | 163 | 145 | – | – | – | – | – | – |  |  | 64
[11 empty] | T12 | F60T12 5' 75W HO | 3 | – | 223 | – | – | – | – | – | – | – |  |  | 65
[11 empty] | T12 | F60T12 5' 75W HO | 4 | – | 278 | 243 | – | – | – | – | – | – |  |  | 66
[11 empty] | T12 | F64T12 64" 80W HO | 1 | – | 104 | – | – | – | – | – | – | – |  |  | 67
[11 empty] | T12 | F64T12 64" 80W HO | 2 | – | 178 | 141 | – | – | – | – | – | – |  |  | 68
[11 empty] | T12 | F64T12 64" 80W HO | 3 | – | 246 | – | – | – | – | – | – | – |  |  | 69
[11 empty] | T12 | F64T12 64" 80W HO | 4 | – | 312 | – | – | – | – | – | – | – |  |  | 70
[11 empty] | T12 | F72T12 6' 168W HO | 1 | – | 169 | – | – | – | – | – | – | – |  |  | 71
[11 empty] | T12 | F72T12 6' 168W HO | 2 | – | 314 | – | – | – | – | – | – | – |  |  | 72
[11 empty] | T12 | F72T12 6' 168W HO | 3 | – | 424 | – | – | – | – | – | – | – |  |  | 73
[11 empty] | T12 | F72T12 6' 57W | 1 | – | 80 | 67 | – | – | – | – | – | – |  |  | 74
[11 empty] | T12 | F72T12 6' 57W | 2 | – | 122 | 106 | – | – | – | – | – | – |  |  | 75
[11 empty] | T12 | F72T12 6' 85W HO | 1 | – | 106 | – | – | – | – | – | – | – |  |  | 76
[11 empty] | T12 | F72T12 6' 85W HO | 2 | – | 190 | 164 | – | – | – | – | – | – |  |  | 77
[11 empty] | T12 | F72T12 6' 85W HO | 3 | – | 291 | 225 | – | – | – | – | – | – |  |  | 78
[11 empty] | T12 | F72T12 6' 85W HO | 4 | – | 323 | – | – | – | – | – | – | – |  |  | 79
[11 empty] | T12 | F84T12 7' 65W | 1 | – | 89 | 75 | – | – | – | – | – | – |  |  | 80
[11 empty] | T12 | F84T12 7' 65W | 2 | – | 143 | 120 | – | – | – | – | – | – |  |  | 81
[11 empty] | T12 | F84T12 7' 100W HO | 1 | – | 113 | – | – | – | – | – | – | – |  |  | 82
[11 empty] | T12 | F84T12 7' 100W HO | 2 | – | 209 | 190 | – | – | – | – | – | – |  |  | 83
[11 empty] | T12 | F84T12 7' 100W HO | 3 | – | 278 | – | – | – | – | – | – | – |  |  | 84
[11 empty] | T12 | F96T12 8' 60W | 1 | – | 74 | 67 | – | – | – | – | – | – |  |  | 85
[11 empty] | T12 | F96T12 8' 60W | 2 | – | 113 | 105 | – | – | – | – | – | – |  |  | 86
[11 empty] | T12 | F96T12 8' 60W | 4 | – | 246 | – | – | – | – | – | – | – |  |  | 87
[11 empty] | T12 | F96T12 8' 75W | 1 | – | 94 | 84 | – | – | – | – | – | – |  |  | 88
[11 empty] | T12 | F96T12 8' 75W | 2 | 145 | 145 | 133 | – | – | – | – | – | – |  |  | 89
[11 empty] | T12 | F96T12 8' 95W HO | 1 | 125 | 120 | – | – | – | – | – | – | – |  |  | 90
[11 empty] | T12 | F96T12 8' 95W HO | 2 | 216 | 203 | 170 | – | – | – | – | – | – |  |  | 91
[11 empty] | T12 | F96T12 8' 110W HO | 1 | 140 | 121 | 119 | – | – | – | – | – | – |  |  | 92
[11 empty] | T12 | F96T12 8' 110W HO | 2 | 258 | 238 | 205 | – | – | – | – | – | – |  |  | 93
[11 empty] | T12 | F95T12 8' 185W HO | 1 | – | 198 | – | – | – | – | – | – | – |  |  | 94
[11 empty] | T12 | F95T12 8' 185W HO | 2 | – | 398 | – | – | – | – | – | – | – |  |  | 95
[11 empty] | T12 | F95T12 8' 185W HO | 3 | – | 550 | – | – | – | – | – | – | – |  |  | 96
[11 empty] | T12 | F95T12 8' 215W HO | 1 | – | 213 | – | – | – | – | – | – | – |  |  | 97
[11 empty] | T12 | F95T12 8' 215W HO | 2 | – | 320 | – | – | – | – | – | – | – |  |  | 98
[11 empty] | T12 | F95T12 8' 215W HO | 3 | – | 518 | – | – | – | – | – | – | – |  |  | 99
[11 empty] | T12 | F96T12 8' 110W HO | 1 | 140 | 121 | 119 | – | – | – | – | – | – |  |  | 100
[11 empty] | T12 | F96T12 8' 110W HO | 2 | 258 | 238 | 205 | – | – | – | – | – | – |  |  | 101
[11 empty] | T12 | F95T12 8' 185W HO | 1 | – | 198 | – | – | – | – | – | – | – |  |  | 102
[11 empty] | T12 | F95T12 8' 185W HO | 2 | – | 398 | – | – | – | – | – | – | – |  |  | 103
[11 empty] | T12 | F95T12 8' 185W HO | 3 | – | 550 | – | – | – | – | – | – | – |  |  | 104
[11 empty] | T12 | F95T12 8' 215W HO | 1 | – | 213 | – | – | – | – | – | – | – |  |  | 105
[11 empty] | T12 | F95T12 8' 215W HO | 2 | – | 320 | – | – | – | – | – | – | – |  |  | 106
[11 empty] | T12 | F95T12 8' 215W HO | 3 | – | 519 | – | – | – | – | – | – | – |  |  | 107
[11 empty] | T8 | F13T8 1' 13W | 1 | – | 17 | – | – | – | – | – | – | – |  |  | 108 | 108
[11 empty] | T8 | F13T8 1' 13W | 2 | – | 36 | – | – | – | – | – | – | – |  |  | 109 | 109
[11 empty] | T8 | F15T8 1.5' 15W | 1 | – | 20 | – | – | – | – | – | – | – |  |  | 110 | 110
[11 empty] | T8 | F15T8 1.5' 15W | 2 | – | 41 | – | – | – | – | – | – | – |  |  | 111 | 111
[11 empty] | T8 | F17T8 2' 17W | 1 | – | 24 | – | – | 18 | – | 13 | 15 | 20 |  |  | 112 | 112
[11 empty] | T8 | F17T8 2' 17W | 2 | – | 45 | – | – | 31 | – | 27 | 30 | 39 |  |  | 113 | 113
[11 empty] | T8 | F17T8 2' 17W | 3 | – | 64 | – | – | 45 | – | 40 | 45 | 59 |  |  | 114 | 114
[11 empty] | T8 | F17T8 2' 17W | 4 | – | 83 | – | – | 57 | – | 53 | 60 | 78 |  |  | 115 | 115
[11 empty] | T8 | F25T8 3' 25W | 1 | – | 30 | – | – | 24 | – | 20 | 22 | 29 |  |  | 116 | 116
[11 empty] | T8 | F25T8 3' 25W | 2 | – | 62 | – | – | 43 | – | 39 | 44 | 58 |  |  | 117 | 117
[11 empty] | T8 | F25T8 3' 25W | 3 | – | 87 | – | – | 63 | – | 63 | 72 | 86 |  |  | 118 | 118
[11 empty] | T8 | F25T8 3' 25W | 4 | – | 116 | – | – | 85 | – | 85 | 74 | 111 |  |  | 119 | 119
[11 empty] | T8 | F25T8 4' 25W | 1 | – | – | – | – | 26 | – | 20 | 22 | 29 |  |  | 120 | 120
[11 empty] | T8 | F25T8 4' 25W | 2 | – | – | – | – | 43 | – | 39 | 44 | 58 |  |  | 121 | 121
[11 empty] | T8 | F25T8 4' 25W | 3 | – | – | – | – | 63 | – | 59 | 66 | 94 |  |  | 122 | 122
[11 empty] | T8 | F25T8 4' 25W | 4 | – | – | – | – | 85 | – | 78 | 88 | 115 |  |  | 123 | 123
[11 empty] | T8 | F28T8 4' 28W | 1 | – | – | – | – | 25 | – | 22 | 25 | 32 |  |  | 124 | 124
[11 empty] | T8 | F28T8 4' 28W | 2 | – | – | – | – | 48 | – | 44 | 49 | 64 |  |  | 125 | 125
[11 empty] | T8 | F28T8 4' 28W | 3 | – | – | – | – | 72 | – | 66 | 74 | 97 |  |  | 126 | 126
[11 empty] | T8 | F28T8 4' 28W | 4 | – | – | – | – | 97 | – | 87 | 99 | 129 |  |  | 127 | 127
[11 empty] | T8 | F30T8 4' 30W ES | 1 | – | 40 | – | – | 31 | – | – | – | – |  |  | 128 | 128
[11 empty] | T8 | F30T8 4' 30W ES | 2 | – | 82 | – | – | 54 | – | – | – | – |  |  | 129 | 129
[11 empty] | T8 | F30T8 4' 30W ES | 3 | – | – | – | – | 77 | – | – | – | – |  |  | 130 | 130
[11 empty] | T8 | F30T8 4' 30W ES | 4 | – | – | – | – | 104 | – | – | – | – |  |  | 131 | 131
[11 empty] | T8 | F32T8 4' 32W | 1 | – | 35 | – | – | 32 | – | 25 | 28 | 37 |  |  | 132 | 132
[11 empty] | T8 | F32T8 4' 32W | 2 | – | 68 | – | 52 | 59 | 77 | 50 | 56 | 74 |  |  | 133 | 133
[11 empty] | T8 | F32T8 4' 32W | 3 | – | 100 | – | 78 | 88 | 115 | 75 | 84 | 110 |  |  | 134 | 134
[11 empty] | T8 | F32T8 4' 32W | 4 | – | 131 | – | 104 | 117 | 153 | 100 | 113 | 147 |  |  | 135 | 135
[11 empty] | T8 | F32T8 4' 32W | 6 | – | – | – | – | – | – | 150 | 169 | 221 |  |  | 136 | 136
[11 empty] | T8 | F32T8 4' 32W | 8 | – | – | – | – | – | – | 200 | 225 | 294 |  |  | 137 | 137
[11 empty] | T8 | F32T8 4' 32W | 12 | – | – | – | – | – | – | 300 | 338 | 442 |  |  | 138 | 138
[11 empty] | T8 | F32T8 4' 32W | 14 | – | – | – | – | – | – | 349 | 394 | 515 |  |  | 139 | 139
[11 empty] | T8 | F32T8 4' 32W | 16 | – | – | – | – | – | – | 399 | 451 | 589 |  |  | 140 | 140
[11 empty] | T8 | F32T8 4' 32W | 18 | – | – | – | – | – | – | 449 | 507 | 662 |  |  | 141 | 141
[11 empty] | T8 | F32T8 4' 32W | 20 | – | – | – | – | – | – | 499 | 563 | 736 |  |  | 142 | 142
[11 empty] | T8 | F32T8 4' 32W VHLO | 3 | – | – | – | – | – | – | – | 279 | – |  |  | 143 | 143
[11 empty] | T8 | F32T8 4' 32W VHLO | 5 | – | – | – | – | – | – | – | 465 | – |  |  | 144 | 144
[11 empty] | T8 | F32T8 4' 32W VHLO | 6 | – | – | – | – | – | – | – | 555 | – |  |  | 145 | 145
[11 empty] | T8 | F32T8 4' 32W VHLO | 8 | – | – | – | – |  | – | – | 793 | – |  |  | 146 | 146
[11 empty] | T8 | F36T8 4' 36W | 2 | – | – | – | – | 74 | – | – | – | – |  |  | 147 | 147
[11 empty] | T8 | F48T8 HO 4' 44W | 1 | – | – | – | – | 59 | – | – | – | – |  |  | 148 | 148
[11 empty] | T8 | F48T8 HO 4' 44W | 2 | – | 120 | – | – | 98 | – | – | – | – |  |  | 149 | 149
[11 empty] | T8 | F40T8 5' 40W | 1 | – | 50 | – | – | 39 | – | – | – | – |  |  | 150 | 150
[11 empty] | T8 | F40T8 5' 40W | 2 | – | 86 | – | – | 75 | – | – | – | – |  |  | 151 | 151
[11 empty] | T8 | F40T8 5' 40W | 3 | – | 131 | – | – | 107 | – | – | – | – |  |  | 152 | 152
[11 empty] | T8 | F40T8 5' 40W | 4 | – | 171 | – | – | 116 | – | – | – | – |  |  | 153 | 153
[11 empty] | T8 | F60T8 HO 5' 55W | 1 | – | – | – | – | 70 | – | – | – | – |  |  | 154 | 154
[11 empty] | T8 | F60T8 HO 5' 55W | 2 | – | 126 | – | – | 118 | – | – | – | – |  |  | 155 | 155
[11 empty] | T8 | F72T8 6' 46W | 1 | – | 52 | – | – | 50 | – | – | – | – |  |  | 156 | 156
[11 empty] | T8 | F72T8 6' 46W | 2 | – | 97 | – | – | 88 | – | – | – | – |  |  | 157 | 157
[11 empty] | T8 | F96T8 8' 59W ES | 1 | – | – | – | – | 64 | – | 47 | 52 | 68 |  |  | 158 | 158
[11 empty] | T8 | F96T8 8' 59W ES | 2 | – | – | – | – | 104 | – | 94 | 104 | 136 |  |  | 159 | 159
[11 empty] | T8 | F72T8 6' 66W HO | 1 | – | – | – | – | 81 | – | – | – | – |  |  | 160 | 160
[11 empty] | T8 | F72T8 6' 66W HO | 2 | – | 150 | – | – | 135 | – | – | – | – |  |  | 161 | 161
[11 empty] | T8 | F96T8 8' 86W HO | 1 | – | – | – | – | 100 | – | – | – | – |  |  | 162 | 162
[11 empty] | T8 | F96T8 8' 86W HO | 2 | – | – | – | – | 160 | – | – | – | – |  |  | 163 | 163
[11 empty] | T8 | F96T8 8' 96W | 1 | – | – | – | – | – | – | 47 | 52 | 68 |  |  | 164 | 164
[11 empty] | T8 | F96T8 8' 96W | 2 | – | – | – | – | – | – | 94 | 104 | 136 |  |  | 165 | 165
[11 empty] | T5 | F4T5 6'' 4W | 1 | – | 9 | – | – | – | – | – | – | – |  |  | 166
[11 empty] | T5 | F4T5 6'' 4W | 2 | – | 20 | – | – | – | – | – | – | – |  |  | 167
[11 empty] | T5 | F6T5 9'' 6W | 1 | – | 10 | – | – | – | – | – | – | – |  |  | 168
[11 empty] | T5 | F6T5 9'' 6W | 2 | – | 21 | – | – | – | – | – | – | – |  |  | 169
[11 empty] | T5 | F8T5 1' 8W | 1 | – | 14 | 10 | – | – | – | – | – | – |  |  | 170
[11 empty] | T5 | F8T5 1' 8W | 2 | – | 23 | 21 | – | – | – | – | – | – |  |  | 171
[11 empty] | T5 | F13T5 2' 13W | 1 | – | 13 | 14 | – | – | – | – | – | – |  |  | 172
[11 empty] | T5 | F13T5 2' 13W | 2 | – | 26 | 27 | – | – | – | – | – | – |  |  | 173
[11 empty] | T5 | F14T5 2' 14W | 1 | – | – | 14 | – | – | – | – | – | – |  |  | 174
[11 empty] | T5 | F14T5 2' 14W | 2 | – | – | 28 | – | – | – | – | – | – |  |  | 175
[11 empty] | T5 | F24T5 HO 2' 24W | 1 | – | – | 27 | – | – | – | – | – | – |  |  | 176
[11 empty] | T5 | F24T5 HO 2' 24W | 2 | – | – | 54 | – | – | – | – | – | – |  |  | 177
[11 empty] | T5 | F21T5 3' 21W | 1 | – | – | 25 | – | – | – | – | – | – |  |  | 178
[11 empty] | T5 | F21T5 3' 21W | 2 | – | – | 49 | – | – | – | – | – | – |  |  | 179
[11 empty] | T5 | F39T5HO 3' 39W | 1 | – | – | 42 | – | – | – | – | – | – |  |  | 180
[11 empty] | T5 | F39T5HO 3' 39W | 2 | – | – | 85 | – | – | – | – | – | – |  |  | 181
[11 empty] | T5 | F28T5 4' 28W | 1 | – | – | 32 | – | – | – | – | – | – |  |  | 182
[11 empty] | T5 | F28T5 4' 28W | 2 | – | – | 63 | – | – | – | – | – | – |  |  | 183
[11 empty] | T5 | F28T5 4' 28W | 3 | – | – | 95 | – | – | – | – | – | – |  |  | 184
[11 empty] | T5 | F28T5 4' 28W | 4 | – | – | 126 | – | – | – | – | – | – |  |  | 185
[11 empty] | T5 | F35T5 5' 35W | 1 | – | – | 40 | – | – | – | – | – | – |  |  | 186
[11 empty] | T5 | 535T5 5' 35W | 2 | – | – | 77 | – | – | – | – | – | – |  |  | 187
[11 empty] | T5 | F54T5HO 4' 54W | 1 | – | – | 62 | – | – | – | – | – | – |  |  | 188
[11 empty] | T5 | F54T5HO 4' 54W | 2 | – | – | 117 | – | – | – | – | – | – |  |  | 189
[11 empty] | T5 | F54T5H0 4' 54W | 3 | – | – | 179 | – | – | – | – | – | – |  |  | 190
[11 empty] | T5 | F54T5HO 4' 54W | 4 | – | – | 234 | – | – | – | – | – | – |  |  | 191
[11 empty] | T5 | F54T5H0 4' 54W | 5 | – | – | 295 | – | – | – | – | – | – |  |  | 192
[11 empty] | T5 | F54T5H0 4' 54W | 6 | – | – | 358 | – | – | – | – | – | – |  |  | 193
[11 empty] | T5 | F54T5H0 4' 54W | 8 | – | – | 468 | – | – | – | – | – | – |  |  | 194
[11 empty] | T5 | F54T5H0 4' 54W | 10 | – | – | 468 | – | – | – | – | – | – |  |  | 195
[11 empty] | T5 | F39T5HO 3' 39W | 1 | – | – | 40 | – | – | – | – | – | – |  |  | 196
[11 empty] | T5 | F39T5HO 3' 39W | 2 | – | – | 77 | – | – | – | – | – | – |  |  | 197
[11 empty] | T5 | F80T5HO 5' 80W | 1 | – | – | 89 | – | – | – | – | – | – |  |  | 198
[11 empty] | CFL | 1 W | 1 | – | 1 | 1 | – | – | – | – | – | – |  |  | 199
[11 empty] | CFL | 2 W | 1 | – | 3 | 2 | – | – | – | – | – | – |  |  | 200
[11 empty] | CFL | 3 W | 1 | – | 4 | 3 | – | – | – | – | – | – |  |  | 201
[11 empty] | CFL | 4 W | 1 | – | 5 | 4 | – | – | – | – | – | – |  |  | 202
[11 empty] | CFL | 5 W | 1 | – | 7 | 5 | – | – | – | – | – | – |  |  | 203
[11 empty] | CFL | 6 W | 1 | – | 8 | 6 | – | – | – | – | – | – |  |  | 204
[11 empty] | CFL | 7 W | 1 | – | 9 | 7 | – | – | – | – | – | – |  |  | 205
[11 empty] | CFL | 8 W | 1 | – | 10 | 8 | – | – | – | – | – | – |  |  | 206
[11 empty] | CFL | 9 W | 1 | – | 12 | 10 | – | – | – | – | – | – |  |  | 207
[11 empty] | CFL | 10 W | 1 | – | 13 | 11 | – | – | – | – | – | – |  |  | 208
[11 empty] | CFL | 11 W | 1 | – | 14 | 12 | – | – | – | – | – | – |  |  | 209
[11 empty] | CFL | 12 W | 1 | – | 16 | 13 | – | – | – | – | – | – |  |  | 210
[11 empty] | CFL | 13 W | 1 | – | 17 | 14 | – | – | – | – | – | – |  |  | 211
[11 empty] | CFL | 14 W | 1 | – | 18 | 15 | – | – | – | – | – | – |  |  | 212
[11 empty] | CFL | 15 W | 1 | – | 20 | 16 | – | – | – | – | – | – |  |  | 213
[11 empty] | CFL | 16 W | 1 | – | 21 | 17 | – | – | – | – | – | – |  |  | 214
[11 empty] | CFL | 17 W | 1 | – | 22 | 18 | – | – | – | – | – | – |  |  | 215
[11 empty] | CFL | 18 W | 1 | – | 24 | 19 | – | – | – | – | – | – |  |  | 216
[11 empty] | CFL | 19 W | 1 | – | 25 | 20 | – | – | – | – | – | – |  |  | 217
[11 empty] | CFL | 20 W | 1 | – | 26 | 21 | – | – | – | – | – | – |  |  | 218
[11 empty] | CFL | 21 W | 1 | – | 27 | 22 | – | – | – | – | – | – |  |  | 219
[11 empty] | CFL | 22 W | 1 | – | 29 | 23 | – | – | – | – | – | – |  |  | 220
[11 empty] | CFL | 23 W | 1 | – | 30 | 24 | – | – | – | – | – | – |  |  | 221
[11 empty] | CFL | 24 W | 1 | – | 31 | 25 | – | – | – | – | – | – |  |  | 222
[11 empty] | CFL | 25 W | 1 | – | 33 | 26 | – | – | – | – | – | – |  |  | 223
[11 empty] | CFL | 26 W | 1 | – | 34 | 28 | – | – | – | – | – | – |  |  | 224
[11 empty] | CFL | 27 W | 1 | – | 35 | 29 | – | – | – | – | – | – |  |  | 225
[11 empty] | CFL | 28 W | 1 | – | 37 | 30 | – | – | – | – | – | – |  |  | 226
[11 empty] | CFL | 29 W | 1 | – | 38 | 31 | – | – | – | – | – | – |  |  | 227
[11 empty] | CFL | 30 W | 1 | – | 39 | 32 | – | – | – | – | – | – |  |  | 228
[11 empty] | CFL | 31 W | 1 | – | 40 | 33 | – | – | – | – | – | – |  |  | 229
[11 empty] | CFL | 32 W | 1 | – | 42 | 34 | – | – | – | – | – | – |  |  | 230
[11 empty] | CFL | 33 W | 1 | – | 43 | 35 | – | – | – | – | – | – |  |  | 231
[11 empty] | CFL | 34 W | 1 | – | 44 | 36 | – | – | – | – | – | – |  |  | 232
[11 empty] | CFL | 35 W | 1 | – | 46 | 37 | – | – | – | – | – | – |  |  | 233
[11 empty] | CFL | 36 W | 1 | – | 47 | 38 | – | – | – | – | – | – |  |  | 234
[11 empty] | CFL | 37 W | 1 | – | 48 | 39 | – | – | – | – | – | – |  |  | 235
[11 empty] | CFL | 38 W | 1 | – | 50 | 40 | – | – | – | – | – | – |  |  | 236
[11 empty] | CFL | 39 W | 1 | – | 51 | 41 | – | – | – | – | – | – |  |  | 237
[11 empty] | CFL | 40 W | 1 | – | 52 | 42 | – | – | – | – | – | – |  |  | 238
[11 empty] | CFL | 41 W | 1 | – | 54 | 43 | – | – | – | – | – | – |  |  | 239
[11 empty] | CFL | 42 W | 1 | – | 55 | 44 | – | – | – | – | – | – |  |  | 240
[11 empty] | CFL | 43 W | 1 | – | 56 | 45 | – | – | – | – | – | – |  |  | 241
[11 empty] | CFL | 44 W | 1 | – | 57 | 47 | – | – | – | – | – | – |  |  | 242
[11 empty] | CFL | 45 W | 1 | – | 59 | 48 | – | – | – | – | – | – |  |  | 243
[11 empty] | CFL | 46 W | 1 | – | 60 | 49 | – | – | – | – | – | – |  |  | 244
[11 empty] | CFL | 47 W | 1 | – | 61 | 50 | – | – | – | – | – | – |  |  | 245
[11 empty] | CFL | 48 W | 1 | – | 63 | 51 | – | – | – | – | – | – |  |  | 246
[11 empty] | CFL | 49 W | 1 | – | 64 | 52 | – | – | – | – | – | – |  |  | 247
[11 empty] | CFL | 50 W | 1 | – | 65 | 53 | – | – | – | – | – | – |  |  | 248
[11 empty] | CFL | 51 W | 1 | – | 67 | 54 | – | – | – | – | – | – |  |  | 249
[11 empty] | CFL | 52 W | 1 | – | 68 | 55 | – | – | – | – | – | – |  |  | 250
[11 empty] | CFL | 53 W | 1 | – | 69 | 56 | – | – | – | – | – | – |  |  | 251
[11 empty] | CFL | 54 W | 1 | – | 71 | 57 | – | – | – | – | – | – |  |  | 252
[11 empty] | CFL | 55 W | 1 | – | 72 | 58 | – | – | – | – | – | – |  |  | 253
[11 empty] | CFL | 56 W | 1 | – | 73 | 59 | – | – | – | – | – | – |  |  | 254
[11 empty] | CFL | 57 W | 1 | – | 74 | 60 | – | – | – | – | – | – |  |  | 255
[11 empty] | CFL | 58 W | 1 | – | 76 | 61 | – | – | – | – | – | – |  |  | 256
[11 empty] | CFL | 59 W | 1 | – | 77 | 62 | – | – | – | – | – | – |  |  | 257
[11 empty] | CFL | 60 W | 1 | – | 78 | 63 | – | – | – | – | – | – |  |  | 258
[11 empty] | CFL | 61 W | 1 | – | 80 | 65 | – | – | – | – | – | – |  |  | 259
[11 empty] | CFL | 62 W | 1 | – | 81 | 66 | – | – | – | – | – | – |  |  | 260
[11 empty] | CFL | 63 W | 1 | – | 82 | 67 | – | – | – | – | – | – |  |  | 261
[11 empty] | CFL | 64 W | 1 | – | 84 | 68 | – | – | – | – | – | – |  |  | 262
[11 empty] | CFL | 65 W | 1 | – | 85 | 69 | – | – | – | – | – | – |  |  | 263
[11 empty] | CFL | 66 W | 1 | – | 86 | 70 | – | – | – | – | – | – |  |  | 264
[11 empty] | CFL | 67 W | 1 | – | 88 | 71 | – | – | – | – | – | – |  |  | 265
[11 empty] | CFL | 68 W | 1 | – | 89 | 72 | – | – | – | – | – | – |  |  | 266
[11 empty] | CFL | 69 W | 1 | – | 90 | 73 | – | – | – | – | – | – |  |  | 267
[11 empty] | CFL | 70 W | 1 | – | 91 | 74 | – | – | – | – | – | – |  |  | 268
[11 empty] | CFL | 71 W | 1 | – | 93 | 75 | – | – | – | – | – | – |  |  | 269
[11 empty] | CFL | 72 W | 1 | – | 94 | 76 | – | – | – | – | – | – |  |  | 270
[11 empty] | CFL | 73 W | 1 | – | 95 | 77 | – | – | – | – | – | – |  |  | 271
[11 empty] | CFL | 74 W | 1 | – | 97 | 78 | – | – | – | – | – | – |  |  | 272
[11 empty] | CFL | 75 W | 1 | – | 98 | 79 | – | – | – | – | – | – |  |  | 273
[11 empty] | CFL | 76 W | 1 | – | 99 | 80 | – | – | – | – | – | – |  |  | 274
[11 empty] | CFL | 77 W | 1 | – | 101 | 81 | – | – | – | – | – | – |  |  | 275
[11 empty] | CFL | 78 W | 1 | – | 102 | 83 | – | – | – | – | – | – |  |  | 276
[11 empty] | CFL | 79 W | 1 | – | 103 | 84 | – | – | – | – | – | – |  |  | 277
[11 empty] | CFL | 80 W | 1 | – | 104 | 85 | – | – | – | – | – | – |  |  | 278
[11 empty] | CFL | 81 W | 1 | – | 106 | 86 | – | – | – | – | – | – |  |  | 279
[11 empty] | CFL | 82 W | 1 | – | 107 | 87 | – | – | – | – | – | – |  |  | 280
[11 empty] | CFL | 83 W | 1 | – | 108 | 88 | – | – | – | – | – | – |  |  | 281
[11 empty] | CFL | 84 W | 1 | – | 110 | 89 | – | – | – | – | – | – |  |  | 282
[11 empty] | CFL | 85 W | 1 | – | 111 | 90 | – | – | – | – | – | – |  |  | 283
[11 empty] | CFL | 86 W | 1 | – | 112 | 91 | – | – | – | – | – | – |  |  | 284
[11 empty] | CFL | 87 W | 1 | – | 114 | 92 | – | – | – | – | – | – |  |  | 285
[11 empty] | CFL | 88 W | 1 | – | 115 | 93 | – | – | – | – | – | – |  |  | 286
[11 empty] | CFL | 89 W | 1 | – | 116 | 94 | – | – | – | – | – | – |  |  | 287
[11 empty] | CFL | 90 W | 1 | – | 118 | 95 | – | – | – | – | – | – |  |  | 288
[11 empty] | CFL | 91 W | 1 | – | 119 | 96 | – | – | – | – | – | – |  |  | 289
[11 empty] | CFL | 92 W | 1 | – | 120 | 97 | – | – | – | – | – | – |  |  | 290
[11 empty] | CFL | 93 W | 1 | – | 121 | 98 | – | – | – | – | – | – |  |  | 291
[11 empty] | CFL | 94 W | 1 | – | 123 | 99 | – | – | – | – | – | – |  |  | 292
[11 empty] | CFL | 95 W | 1 | – | 124 | 101 | – | – | – | – | – | – |  |  | 293
[11 empty] | CFL | 96 W | 1 | – | 125 | 102 | – | – | – | – | – | – |  |  | 294
[11 empty] | CFL | 97 W | 1 | – | 127 | 103 | – | – | – | – | – | – |  |  | 295
[11 empty] | CFL | 98 W | 1 | – | 128 | 104 | – | – | – | – | – | – |  |  | 296
[11 empty] | CFL | 99 W | 1 | – | 129 | 105 | – | – | – | – | – | – |  |  | 297
[11 empty] | CFL | 100 W | 1 | – | 131 | 106 | – | – | – | – | – | – |  |  | 298
[11 empty] | HPS | 35W Med. Base | 1 | – | – | 43 | – | – | – | – | – | – |  |  | 299
[11 empty] | HPS | 50W Med. Base | 1 | – | – | 64 | – | – | – | – | – | – |  |  | 300
[11 empty] | HPS | 70W Med. Base | 1 | – | – | 86 | – | – | – | – | – | – |  |  | 301
[11 empty] | HPS | 70W Med. Base | 1 | – | – | 126 | – | – | – | – | – | – |  |  | 302
[11 empty] | HPS | 100W Mogul Base | 1 | – | – | 130 | – | – | – | – | – | – |  |  | 303
[11 empty] | HPS | 150W Med. Base | 1 | – | – | 188 | – | – | – | – | – | – |  |  | 304
[11 empty] | HPS | 150W Mogul Base | 1 | – | – | 188 | – | – | – | – | – | – |  |  | 305
[11 empty] | HPS | 200W Mogul Base | 1 | – | – | 240 | – | – | – | – | – | – |  |  | 306
[11 empty] | HPS | 250W Mogul Base | 1 | – | – | 295 | – | – | – | – | – | – |  |  | 307
[11 empty] | HPS | 310W Mogul Base | 1 | – | – | 365 | – | – | – | – | – | – |  |  | 308
[11 empty] | HPS | 400W Mogul Base | 1 | – | – | 457 | – | – | – | – | – | – |  |  | 309
[11 empty] | HPS | 600W Mogul Base | 1 | – | – | 665 | – | – | – | – | – | – |  |  | 310
[11 empty] | HPS | 750W Mogul Base | 1 | – | – | 840 | – | – | – | – | – | – |  |  | 311
[11 empty] | HPS | 1000W Mogul Base | 1 | – | – | 1100 | – | – | – | – | – | – |  |  | 312
[11 empty] | MV | 50W Med. Base | 1 | 75 | – | – | – | – | – | – | – | – |  |  | 313
[11 empty] | MV | 75W Med. Base | 1 | 75 | – | – | – | – | – | – | – | – |  |  | 314
[11 empty] | MV | 100W Med. Base | 1 | 122 | – | – | – | – | – | – | – | – |  |  | 315
[11 empty] | MV | 175W Med. Base | 1 | 205 | – | – | – | – | – | – | – | – |  |  | 316
[11 empty] | MV | 175W Mogul Base | 1 | 205 | – | – | – | – | – | – | – | – |  |  | 317
[11 empty] | MV | 250W Mogul Base | 1 | 285 | – | – | – | – | – | – | – | – |  |  | 318
[11 empty] | MV | 400W Mogul Base | 1 | 454 | – | – | – | – | – | – | – | – |  |  | 319
[11 empty] | MV | 400W Mogul Base | 1 | 880 | – | – | – | – | – | – | – | – |  |  | 320
[11 empty] | MV | 1,000W Mogul Base | 1 | 1080 | – | – | – | – | – | – | – | – |  |  | 321
[11 empty] | MH | 32W Med. Base | 1 | 38 | – | – | – | – | – | – | – | – |  |  | 322
[11 empty] | MH | 35W/39W Med. Base | 1 | 48 | – | – | – | – | – | – | – | – |  |  | 323
[11 empty] | MH | 50W Med. Base | 1 | 62 | – | – | – | – | – | – | – | – |  |  | 324
[11 empty] | MH | 70W Med. Base | 1 | 93 | – | – | – | – | – | – | – | – |  |  | 325
[11 empty] | MH | 70W Double Ended | 1 | 94 | – | – | – | – | – | – | – | – |  |  | 326
[11 empty] | MH | 100W Med. Base | 1 | 125 | – | – | – | – | – | – | – | – |  |  | 327
[11 empty] | MH | 100W Double Ended | 1 | 130 | – | – | – | – | – | – | – | – |  |  | 328
[11 empty] | MH | 175W Mogul Base | 1 | 210 | – | – | – | – | – | – | – | – |  |  | 329
[11 empty] | MH | 150W Med. Base | 1 | 173 | – | – | – | – | – | – | – | – |  |  | 330
[11 empty] | MH | 150W Double Ended | 1 | 185 | – | – | – | – | – | – | – | – |  |  | 331
[11 empty] | MH | 250W Mogul Base | 1 | 295 | – | – | – | – | – | – | – | – |  |  | 332
[11 empty] | MH | 400W Mogul Base | 1 | 456 | – | – | – | – | – | – | – | – |  |  | 333
[11 empty] | MH | 400W Mogul Base | 1 | 890 | – | – | – | – | – | – | – | – |  |  | 334
[11 empty] | MH | 1000W Mogul Base | 1 | 1080 | – | – | – | – | – | – | – | – |  |  | 335
[11 empty] | MH | 1500W Mogul Base | 1 | 1610 | – | – | – | – | – | – | – | – |  |  | 336
[11 empty] | MH | 1650W Mogul Base | 1 | 1765 | – | – | – | – | – | – | – | – |  |  | 337
[11 empty] | MH | 2000W Mogul Base | 1 | 2140 | – | – | – | – | – | – | – | – |  |  | 338
[11 empty] | MV Canopy/Soffit | 100 Watt | 1 | 122 | – | – | – | – | – | – | – | – |  |  | 339
[11 empty] | MV Canopy/Soffit | 175 Watt | 1 | 205 | – | – | – | – | – | – | – | – |  |  | 340
[11 empty] | MV Canopy/Soffit | 250 Watt | 1 | 285 | – | – | – | – | – | – | – | – |  |  | 341
[11 empty] | MV Canopy/Soffit | 400 Watt | 1 | 454 | – | – | – | – | – | – | – | – |  |  | 342
[11 empty] | MH Canopy/Soffit | 100 Watt | 1 | 130 | – | – | – | – | – | – | – | – |  |  | 343
[11 empty] | MH Canopy/Soffit | 150 Watt | 1 | 188 | – | – | – | – | – | – | – | – |  |  | 344
[11 empty] | MH Canopy/Soffit | 200 Watt | 1 | 240 | – | – | – | – | – | – | – | – |  |  | 345
[11 empty] | MH Canopy/Soffit | 250 Watt | 1 | 295 | – | – | – | – | – | – | – | – |  |  | 346
[11 empty] | MH Canopy/Soffit | 310 Watt | 1 | 365 | – | – | – | – | – | – | – | – |  |  | 347
[11 empty] | MH Canopy/Soffit | 400 Watt | 1 | 457 | – | – | – | – | – | – | – | – |  |  | 348
[11 empty] | HPS Canopy/Soffit | 100 Watt | 1 | 130 | – | – | – | – | – | – | – | – |  |  | 349
[11 empty] | HPS Canopy/Soffit | 150 Watt | 1 | 188 | – | – | – | – | – | – | – | – |  |  | 350
[11 empty] | HPS Canopy/Soffit | 200 Watt | 1 | 240 | – | – | – | – | – | – | – | – |  |  | 351
[11 empty] | HPS Canopy/Soffit | 250 Watt | 1 | 295 | – | – | – | – | – | – | – | – |  |  | 352
[11 empty] | HPS Canopy/Soffit | 310 Watt | 1 | 365 | – | – | – | – | – | – | – | – |  |  | 353
[11 empty] | HPS Canopy/Soffit | 400 Watt | 1 | 457 | – | – | – | – | – | – | – | – |  |  | 354
[11 empty] | MV Wall Pack | 50 Watt | 1 | 75 | – | – | – | – | – | – | – | – |  |  | 355
[11 empty] | MV Wall Pack | 75 Watt | 1 | 95 | – | – | – | – | – | – | – | – |  |  | 356
[11 empty] | MV Wall Pack | 100 Watt | 1 | 120 | – | – | – | – | – | – | – | – |  |  | 357
[11 empty] | MV Wall Pack | 175 Watt | 1 | 205 | – | – | – | – | – | – | – | – |  |  | 358
[11 empty] | MV Wall Pack | 250 Watt | 1 | 285 | – | – | – | – | – | – | – | – |  |  | 359
[11 empty] | MV Wall Pack | 400 Watt | 1 | 454 | – | – | – | – | – | – | – | – |  |  | 360
[11 empty] | MH Wall Pack | 35 Watt | 1 | 48 | – | – | – | – | – | – | – | – |  |  | 361
[11 empty] | MH Wall Pack | 50 Watt | 1 | 62 | – | – | – | – | – | – | – | – |  |  | 362
[11 empty] | MH Wall Pack | 70 Watt | 1 | 93 | – | – | – | – | – | – | – | – |  |  | 363
[11 empty] | MH Wall Pack | 100 Watt | 1 | 125 | – | – | – | – | – | – | – | – |  |  | 364
[11 empty] | MH Wall Pack | 150 Watt | 1 | 173 | – | – | – | – | – | – | – | – |  |  | 365
[11 empty] | MH Wall Pack | 175 Watt | 1 | 210 | – | – | – | – | – | – | – | – |  |  | 366
[11 empty] | MH Wall Pack | 250 Watt | 1 | 295 | – | – | – | – | – | – | – | – |  |  | 367
[11 empty] | MH Wall Pack | 400 Watt | 1 | 454 | – | – | – | – | – | – | – | – |  |  | 368
[11 empty] | HPS Wall Pack | 35 Watt | 1 | 43 | – | – | – | – | – | – | – | – |  |  | 369
[11 empty] | HPS Wall Pack | 50 Watt | 1 | 64 | – | – | – | – | – | – | – | – |  |  | 370
[11 empty] | HPS Wall Pack | 70 Watt | 1 | 86 | – | – | – | – | – | – | – | – |  |  | 371
[11 empty] | HPS Wall Pack | 100 Watt | 1 | 126 | – | – | – | – | – | – | – | – |  |  | 372
[11 empty] | HPS Wall Pack | 150 Watt | 1 | 188 | – | – | – | – | – | – | – | – |  |  | 373
[11 empty] | HPS Wall Pack | 200 Watt | 1 | 240 | – | – | – | – | – | – | – | – |  |  | 374
[11 empty] | HPS Wall Pack | 250 Watt | 1 | 295 | – | – | – | – | – | – | – | – |  |  | 375
[11 empty] | HPS Wall Pack | 310 Watt | 1 | 365 | – | – | – | – | – | – | – | – |  |  | 376
[11 empty] | HPS Wall Pack | 400 Watt | 1 | 457 | – | – | – | – | – | – | – | – |  |  | 377
[11 empty] | CFL Pin | 32W | 2 | 68 | – | 68 | – | – | – | – | – | – |  |  | 378
[11 empty] | CFL Pin | 38 W | 2 | 74 | – | 74 | – | – | – | – | – | – |  |  | 379
[11 empty] | CFL Pin | 42 W | 2 | 93 | – | 93 | – | – | – | – | – | – |  |  | 380